## MATRIX
-> data.csv
section | no | parameter | requirement | Hopewind | Hoymiles | Delta | FIMER (PVS980-58BC, 2500 kVA) | Newen (CPS 1500/3000_260817-R0) | Sineng (EH-1250-HC-UD / EH-1725-HB-UD) | Inovance (IES920-07-2500-C-D-EU) | ENERZOLVE | Sifang (CSD-5831, 2500 kVA) | Kehua (BCS1250K-C-HUD, 2 × 1.25 MW)
Performance Envelope | 1 | Peak efficiency | ≥ 99.0 % | 98.5 | 99 | 99 | 98.8 | 99.21 | 99 | 99 | 98.5 | 98.8% | 99% max. efficiency
Performance Envelope | 2 | Euro / CEC efficiency | ≥ 98.5 % | NA | 98.5 | 98.5 | 98.6 | 99.03 | 98 | 98.3 | NA | NA | Not stated
Performance Envelope | 3 | Power factor range | 0.9 lead – 0.89 lag | -1 to +1 | -1 to +1 | ~-0.89 to +0.9 | -1 to +1 | -1 to +1 | -1 to +1 | ~-0.89 to +0.9 | -1 to +1 | -1 to +1 | 1 leading to 1 lagging (adjustable)
Performance Envelope | 4 | Response time (P/Q) | < 50 ms | 30 | 50 | 150 | NA | 50 | 50 | 50 | NA | ≤20 ms | 49 ms charging; 53 ms discharging (single PCS)
Performance Envelope | 5 | Grid-forming step response | < 5 ms | 200 | 5 | NA | NA | 5 | 5 | NA | NA | NA | Not stated
Performance Envelope | 6 | Design / service life | ~ 15 - 20 years | 20 | 20 | 20 | 25 | 20 | 25 | 20 | 20 | ≥25 years | ≥25 years (supplier-stated)
Product Range | 7 | String PCS | 50 – 250 kW | NA | NA | NA | NA | NA | NA | 400kW and 430kW | NA | NA | NA
Product Range | 8 | Modular PCS | 250 kW – 1.5 MW | NA |  | Base model Capacity - 1.1MW and 1.25MW | NA | NA | NA | 400kW,430kW and 432kW | NA | 2 × 1.25 MW battery branches | 2 × 1.25 MW battery branches
Product Range | 9 | Central PCS | 1.5 – 5 MW | 2.5MW @50 deg | 2.5MVA | By paralleling the modular PCS, total capacity can be enhanced upto 6.25MW | 869–5000 kVA range (2028–2210 kVA @50°C for 2500-L) | 0.69MW~1.59MW/1.39MW~3.18MW | 1 - EH-1250-HC-UD 2 - EH-1725-HB-UD | 1.5 – 5 MW | 1.5 – 5 MW | CSD-5831: 2500 kVA; 2500 kVA @50°C; 2750 kVA @35°C | 2.5 MW (2 × 1.25 MW); 2.5 MVA at 50°C; 2.75 MVA at 35°C
Product Range | 10 | Redundancy | N+1 at utility scale | Yes | NA | Yes | NA | Yes | Yes | Yes | Yes | NA | Not stated
AC Interface | 11 | Nominal AC voltage | 400 V / 690 V | 690 V | 690V | Modular PCS - 690VAC | 480 / 520 / 560 / 600 / 630 / 660 / 690 V | 350~800Vac ± 10% | 607~759V | 690Vac | 690V | 690 V | 690 Vac, 3P3W+PE
AC Interface | 12 | Frequency | 50 / 60 Hz ± configurable | 50Hz | 50 / 60 Hz ± configurable | 50Hz | 50/60 Hz (±10 Hz) | 50/60Hz ± 10% | 50Hz/ 45~55Hz | 50 / 60 Hz ± configurable | 50/60 | 50 Hz; grid frequency range 45–55 Hz | 50/60 Hz; 50 Hz grid range 45–55 Hz
AC Interface | 13 | THD (current) | < 3 % at rated power | <3% | <3% | <3% | < 3 % | <3% | <3% | <3% | <3% | <3% at nominal power | <3% at rated power
AC Interface | 14 | DC injection | < 0.5 % of rated current | 0.5% of rated current | 0.5% of rated current | 0.5% of rated current | NA | 0.5% of rated current | < 0.5 % of rated current | 0.5% of rated current | 0.5% of rated current | DC-component protection stated; numerical DC injection limit not stated | Numerical DC-injection limit not stated
AC Interface | 15 | Overload capability | 110 % continuous; 120 % for 60 s | 110% long term,120 for 10 sec,150% for 1sec | 110 % continuous; 120 % for 60 s | Complied 110% continuous at 30°C. | Not specified in datasheet | 110% for 10sec | 110 % for 10 mins ; 120 % for 2 mins | 110 % continuous; 120 % for 60 s | To be confirmed. | 110% continuous; 120% for 1 min (35°C); full load supported at 50°C | 110% overload; duration not stated in datasheet
DC Interface | 16 | DC voltage window | 600 – 1500 V | 1000-1500 V DC | 1000-1500 | 1000V - 1500VDC | 680–1500 V (Umax 1500 V) | 511-1500Vdc | 1000 - 1500 Vdc | 1000-1500V | 1000-1500V | 1000–1500 Vdc; max DC voltage 1500 V | 1000–1500 Vdc; max 1500 Vdc
DC Interface | 17 | Insulation monitoring | Continuous | NA | Continuous | Continuous | Not specified in datasheet | Optional | Continuous | Continuous | To be confirmed. | Continuous | Online insulation detection
DC Interface | 18 | DC precharge / softstart | Standard | Standard | Standard | Standard | Not specified in datasheet | Standard | Standard | Standard | Standard | NA | Soft start: Yes; DC pre-charge circuit equipped
DC Interface | 19 | Reverse-polarity protection | Mandatory | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Not stated
Mechanical | 20 | Ingress protection | IP54, IP65 optional | IP 66 | IP65 | IP65 | IP65 electronics / IP55 rest; Type 3R | IP65 Outdoor | IP65 complied | IP65 | IP54 | IP65 | IP65
Mechanical | 21 | Corrosion class | C4 standard; C5-M optional | C5 | C4 | C4 | NA | C5 | C4 | C4 | C4 | Anti-corrosion treatment stated; corrosion class not stated | Corrosion class not stated; anti-corrosion treatment stated
Mechanical | 22 | Seismic qualification | IEEE 693 or equivalent | Certification N/A | NA | Yes | NA | Yes | NA | Yes | Yes | Shock/vibration/seismic-strength requirements stated; formal seismic qualification not stated | Formal seismic qualification not stated
Thermal | 23 | Ambient (full power target) | ≥ 50 °C without derating | 2.5MW @50 deg | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes – full load at 50°C | 2 PCS parallel: 100% load to 45°C at ≤2000 m altitude; 50°C is derated
Thermal | 24 | Max ambient (operational) | − 20 °C to + 60 °C | -40 to +60 deg | − 20 °C to + 60 °C | − 20 °C to + 60 °C | − 20 °C to + 60 °C | -25°C to 60°C (>51°C de-rated) | -40~60degC | -40 °C to + 60 °C | ~ -30 C to +60 C | -35°C to +60°C; derating >50°C | -35°C to +60°C; >50°C derating
Thermal | 25 | Cooling method | Forced air / liquid per class | Liquid cooled | Liquid cooling | Complied | Patented self-contained thermosyphon (liquid-cooled ratings, air-cooling simplicity) | Forced Air | advanced 2 phase + forced air cooling | Air-liquid cooling | Intelligent/forced air (hybrid) cooling | Intelligent forced-air cooling | Intelligent air cooling
Thermal | 26 | Filter / maintenance | Tool-free, long interval | N/A for air filter | As per site condition | Tool free, interval 1 month | Low maintenance, no fillable liquids/pumps/valves | Yes | complied | Complied | Not met | Not stated | Filter/maintenance interval not stated
Thermal | 27 | Cooling redundancy | Fan N+1 at utility scale | N/A, only possible for extra spare part | No redundancy | Not Available | Not specified in datasheet | Adequate | Yes | Will have one spare Fan on site | Not met | Not stated | Fan redundancy not stated; DC and AC fans provided
Thermal | 28 | Altitude | Up to 3000 m with derating | 4000 mtr | up to 5000 mts | Complied | 4000 m (2000 m std, 4000 m option) | Up to 4000mts (>2000mts de-rated) | 5000m （>3000 m derating） | Complied | Rated to 4000 m (derating above 2000 m) | 5000 m; derating >3000 m | Up to 4000 m; derating above 2000 m
Environmental | 29 | Ambient temp | − 20 °C to + 60 °C | -40 to +60 deg | Complied | Complied | −20 … +60 °C | -25°C to 60°C (>51°C de-rated) | -40~60degC | -40 °C to + 60 °C | ~ -30 C to +60 C | -35°C to +60°C | -35°C to +60°C
Environmental | 30 | Humidity | 0 – 100 % condensing (protected) | 4-100% | Complied | Complied with 0% to 100% RH, non-condensing | 4 … 100 % | 0~95% Non-condensing - Standard (Up to 100% optional) | 0-100% | Complied | To be confirmed. | 0–100% RH, non-condensing | 0–100% RH, non-condensing
Environmental | 31 | Pollution / dust | High-dust capable | Complied | Complied | Complied | Sand test certified / dust proof outdoor enclosure | Yes | 30PPI dustproof cotton | Complied | IP54 | Dust/wind/sand protection stated; numerical dust class not stated | Dust/salt/extreme-environment capability stated; numerical dust class not stated
Battery Compatibility | 32 | Chemistry | LFP primary & Na-ion capable | LFP,Li | Complied | Complied | Battery DC input (chemistry-agnostic) | Yes | complied |  | Complied | Battery chemistry not stated | Battery chemistry not stated; compatible DC input
Battery Compatibility | 33 | Voltage window | 600 – 1500 V DC configurable | 1000-1500 V DC | 1000-1500 | Complied with 1000V - 1500VDC | 680–1500 V DC | 511~1500Vdc | 1000 - 1500 Vdc |  | Complied | 1000–1500 Vdc | 1000–1500 Vdc
Battery Compatibility | 34 | BMS interface | CAN / Modbus / open protocol | CAN / Modbus | CAN/Modbus | NA | Not specified in datasheet (via I/O) | Modbus TCP/IP | CAN |  | CAN / Modbus / Ethernet | CAN available; BMS-specific interface/protocol not explicitly stated | CAN; BMS-specific protocol not stated
Battery Compatibility | 35 | Charge control | CC-CV, CP | CC - CV - CP | EMS should send command to PCS | Complied | Controlled by external control system | Yes | complied |  | Complied | Constant-voltage, constant-current and constant-power charge/discharge | Charge/discharge control; CC-CV/CP not explicitly stated
Communication | 36 | Modbus TCP/RTU | Mandatory | Compllied | Complied | Complied | Modbus | Modbus TCP/IP | complied | Complied | Modbus-RTU and Modbus-TCP supported. | Modbus supported | Modbus-RTU and Modbus-TCP
Communication | 37 | IEC 61850 | Mandatory (utility) | Complied | Complied | NA | Not specified in datasheet | Not mandatory for PCS | Complied as per IEC 104 and TCP -IP | Complied | Complied | IEC 61850 supported | IEC 61850 supported
Communication | 38 | DNP3 | Recommended | NA | NA | NA | Not specified in datasheet | Not mandatory for PCS | 2. PCS to EMS/SCADA/any master: Modbus TCP/IP （RJ 45 port, CAT 6 cable） Modbus RTU （RS485 port, twisted pair cable) | Not available | Not available | NA – DNP3 not stated | DNP3 not stated
EMS / SCADA | 39 | Control interface | P/Q setpoints, ramp, mode change remotely | Complied through EMS | Complied | Complied | Active/reactive power controlled by external control system | Comply | 2. PCS to EMS/SCADA/any master: Modbus TCP/IP （RJ 45 port, CAT 6 cable） Modbus RTU （RS485 port, twisted pair cable) |  | Comply | RS485, Ethernet, CAN, dry-contact interfaces | P/Q setpoints, ramp and mode control via EMS/SCADA; RS485/Ethernet/CAN/dry contacts
EMS / SCADA | 40 | Applications | Peak shaving, arbitrage, freq. regulation, RE smoothing | Complied | Complied | Complied | Peak shaving, grid support, RE smoothing (BESS applications) | Comply | can be discussed during detailed engineering |  | Comply | Peak shaving, frequency regulation, peak shaving/valley filling, island operation | Peak shaving, frequency modulation, auxiliary grid connection/new-energy applications
EMS / SCADA | 41 | SCADA protocol | IEC 61850 / DNP3 | DNP NA | IEC61850 | Not Available | Not specified (Modbus/Profinet/Ethernet IP available) | Comply to EMS | 2. PCS to EMS/SCADA/any master: Modbus TCP/IP （RJ 45 port, CAT 6 cable） Modbus RTU （RS485 port, twisted pair cable) |  | In-Progress | CAN2.0B, Modbus, IEC 61850, GOOSE, IEC 104 | IEC 61850 / Modbus-TCP/RTU; DNP3 not stated
EMS / SCADA | 42 | SCADA redundancy | Dual comms path | Complied |  | Complied | Not specified in datasheet | Comply to EMS | Kindly Explain |  | In-Progress | Not stated | Double Web ETH network port; SCADA redundancy architecture not explicitly stated
Grid-Forming | 43 | Voltage-source behaviour | Mandatory | Complied | Complied | Complied | Grid support functions (reactive power, FRT) | Capable | complied | Complied | Compliant — Grid-forming voltage-source mode (off-grid rated 630 V, 3W+PE). | VSG and VF; island mode supplies fixed-frequency/voltage AC | GFM equipped per supplier response; off-grid 690 Vac operation
Grid-Forming | 44 | Virtual inertia | Configurable H | Available for nov-2026 | Complied | Not Available | Not specified in datasheet | Yes | complied | 1~10s configurable | Compliant | NA – virtual inertia not explicitly stated | Not stated
Grid-Forming | 45 | Black-start | Mandatory | Complied | Complied | Complied | Not specified in datasheet | Yes | complied | Complied | Compliant — GFM / off-grid capability supports black-start | Yes | Black-start supported per supplier response
Grid-Forming | 46 | Islanding / microgrid | Seamless | Complied | Seamless not available while switcing mode between two modes | Can be discussed during detailed engg. | Not specified in datasheet | 160~300ms | complied | Complied | Compliant — On/off-grid (GFL/GFM) operation supported; seamless microgrid transition to be confirmed by test. | Yes – grid-connected and island modes; stable voltage/frequency in island mode | On/off-grid capability; seamless transition timing not stated
Grid-Forming | 47 | Fault current contribution | Defined, sustained |  | Max 8000A | as per CEA guideline | Max AC short circuit current 66 kA (1 s RMS) | • Stady-state short circuit current (rms) (Iₖ): In 9-12ms the inverter current becomes zero. Therefore, Iₖ ≈ Zero (negligible). • Initial short circuit current (rms)(Iₖ"): RMS value of first 20ms Iₖ" = 2595A for CPS 3 MW. • Peak short circuit current (Iₚ) = 18.3kA for CPS 3 MW.Stady-state short circuit current (rms) (Iₖ): In 9-12ms the inverter current becomes zero. Therefore, Iₖ ≈ Zero (negligible). • Initial short circuit current (rms)(Iₖ"): RMS value of first 20ms Iₖ" = 2595A for CPS 3 MW. • Peak short circuit current (Iₚ) = 18.3kA for CPS 3 MW. | complied | Ik=2.3kA | Compliant | AC-side short-circuit capacity 55 kA; DC-side 250 kA. Fault-current injection waveform not stated | Not stated
Grid-Following | 48 | Current-source control | Mandatory | Complied | Complied | Complied | Yes | Yes | complied | Complied | Compliant — Grid-following current-source control supported. | PQ/grid-connected current control supported; exact current-source mode terminology not stated | Grid-following current-source mode not explicitly stated
Grid-Following | 49 | PLL robustness | Weak-grid capable (SCR ≥ 1.5) | Complied | Complied | complied | Not specified in datasheet | SCR 3 | complied | Complied | Compliant — Weak-grid capability (SCR >= 1.5) | PSSE PLL model included; T_PLLANG example 0.01 s; SCR value not stated | PLL robustness / SCR not stated
Grid-Following | 50 | LVRT / HVRT | Full ride-through | Complied | Complied as per CEA | Complied | LVRT & HVRT | Yes | complied | Complied | Compliant — LVRT/HVRT full ride-through per IEEE 1547 / UL 1741 SA. | Yes – LVRT/HVRT functions and PSSE/PSCAD/HIL benchmark | LVRT: supplier response says meet CEA Grid Code; curve/report not supplied
Grid-Following | 51 | Frequency response | P(f) droop configurable | Complied | Complied | Complied | FqRT / power reduction | Yes | complied | Complied | Compliant — P(f) droop configurable (UL 1741 SA). | Primary frequency control demonstrated; 50.4 Hz → -0.2 pu P and 49.6 Hz → +0.2 pu P; 50.05/49.96 Hz deadband in benchmark | LFRT: 47.5–52 Hz; rated output maintained 49.5–50.5 Hz
Grid-Following | 52 | Volt-VAr / Volt-Watt | Configurable curves |  | Complied | Complied | Reactive power compensation | Yes | complied | Complied | Compliant — Volt-VAr / Volt-Watt configurable curves (UL 1741 SA). | Q(U) droop / Volt-VAr control supported in PSSE model | Volt-VAr / Volt-Watt curves not stated
Grid-Code Functions | 53 | Fault ride-through | LVRT & HVRT curves | Complied | Complied as per CEA | Complied | LVRT, HVRT, FRT with current feed-in | Yes | complied | Complied with CEA | Compliant — LVRT & HVRT ride-through per IEEE 1547 / UL 1741 SA. | Yes – LVRT/HVRT/FRT benchmarked | LVRT/HVRT/FRT: CEA Grid Code stated; detailed curves not supplied
Grid-Code Functions | 54 | Reactive support | Q at zero P capability | Complied | Complied | Complied | Reactive power at night with DC disconnected | 100% - Four quadrant | complied | 2612 kVar | Compliant — PQ curve shows full reactive capability at zero active power. | ±100% reactive power range; Q(U) droop | Four-quadrant P/Q; 2×PCS: approx. ±2500 kVAr at 50°C
Grid-Code Functions | 55 | Frequency response | FFR / droop | Complied | Complied | Complied | FqRT / droop | Yes, aligned with IEEE 2800-2022 recommendations | complied | Complied | Compliant — FFR / frequency droop supported (UL 1741 SA). | Yes – primary frequency control | Frequency response/droop not stated
Grid-Code Functions | 56 | Ramp-rate control | Configurable | Complied | Complied | Complied | Power reduction / active power limitation | Yes | complied | full-load charge/ discharge switchover within 30 ms | Compliant — Configurable ramp-rate control via EMS. | PSSE model example 5 pu/s; benchmark tested at 0.1 pu/s | Ramp rate settable in PCS
Grid Code | 57 | India | CEA / CERC connectivity regs | CEA | Complied as per CEA | Complied | IEC & CEA (India) | CEA 2022 latest regulation | complied as per Latest CEA guidelines | Complied with CEA | To be confirm after the compliance the test | CEA certification available | CEA Grid Code stated in supplier response; certificate not supplied
International Standards | 58 | Inverter design/test | IEC 62109-1/-2 | Complied | Not applicable for BESS PCS | Complied with equivalent standard IEC 62477 | Not specified (IEC 62477-1 declared) | IEC 62909-1&2 | complied as per IEC62477-1 | Complied | To be confirm after the compliance the test | IEC 62477-1 certified | IEC 62477-1
International Standards | 59 | Grid interconnection | IEC 62477, IEEE 1547 | coomplied | Complied as per IEC62477-1 | Complied | IEC 62477-1 | IEC 62477-1, IEC 61727 & IEC 62116 | complied as per IEC 62477 | Complied with IEC 62477.Will provide IEEE 1547 certificate if mandatory. | To be confirm after the compliance the test | IEC 62909-1 stated in datasheet; IEC 61727/62116 certificates available | IEC 62477-1, IEC 61727, IEC 62116; IEEE 1547 not stated
International Standards | 60 | BESS system | IEC 62933 series | Complied | Applicable for BESS not for PCS | NA | Not specified in datasheet | Not applicable for PCS alone | NA | Complied | To be confirm after the compliance the test | NA – no IEC 62933/system-level certificate in provided documents | IEC 62933 not stated
International Standards | 61 | Environmental test | IEC 60068 series | Complie d | Complied | Complied | IEC 60068-2-1,-2,-14,-30 | IEC 60068-2-1, 2, 11, 14 & 30 | complied | Complied | To be confirm after the compliance the test | IEC 60068-2-1/-2/-14/-30 certified | IEC 60068-2-1/-2/-14/-30
EMC | 62 | Emissions | IEC 61000-6-4 (industrial) | Complied | Complied | Complied | EN 50530 / IEC 61727 / IEC 62116 (EMC per CE) | Comply | complied | Complied | To be confirm after the compliance the test | EN IEC 61000-6-4:2019 certificate | EN IEC 61000-6-2; EN55011 stated
EMC | 63 | Immunity | IEC 61000-6-2 | Complied | Complied | Complied | CE Declaration of Conformity | Comply | complied | Complied | To be confirm after the compliance the test | EN IEC 61000-6-2:2019 certificate | EN IEC 61000-6-2
EMC | 64 | Harmonics / flicker | IEC 61000-3 series | NA, Complied as per CEA | NA | Complied with equivalent standard such as IEEE 519 | Not specified in datasheet | CEA 2022 latest regulation | complied as per Latest CEA guidelines | Not available | To be confirm after the compliance the test | THDi <3%; IEEE 519 and CEA certification; no numerical flicker result provided | THDi <3%; numerical individual harmonic/flicker data not stated
EMC | 65 | Surge | IEC 61000-4 series | Type I+II complied | Complied | Complied | Heavy duty (Type 1) surge protection option | CEA 2022 latest regulation | complied as per Latest CEA guidelines | Not available | To be confirm after the compliance the test | Lightning/surge protection stated; dedicated surge-test result not provided | Surge/lightning protection stated; test result not supplied
Safety | 66 | Electrical safety | IEC 62109 / IEC 61010 | Complied as per IEC 62477-1 | Complied as per IEC62477-1 | Complied with euivalent standard IEC 62477 | IEC 62477-1 | IEC 62909-1&2 | complied as per IEC62477-1 | Complied with IEC 62109 | To be confirm after the compliance the test | IEC 62477-1 certificate | IEC 62477-1
Safety | 67 | Emergency stop | Hardwired E-stop | Complied | Complied | Complied | Not specified in datasheet | Yes | complied | Complied | Compliant — Hardwired E-stop provided; AC breaker with shunt trip. | Not stated | Emergency stop not stated
Protection Functions | 68 | Over/under voltage | Mandatory | Complied | Complied | Complied | Grid monitoring / AC & DC over voltage: Yes | Yes | complied | Complied | Compliant — AC over/under-voltage and DC over-voltage protection included. | Yes | AC/DC over-voltage protection stated; thresholds not supplied
Protection Functions | 69 | Over/under frequency | Mandatory | Complied | Complied | Complied | Grid monitoring: Yes | Yes | complied | Complied | Compliant — AC over/under-frequency protection included. | Yes | Over/under-frequency protection not specifically stated
Protection Functions | 70 | Overcurrent | Mandatory | Complied | Complied | Complied | AC & DC short circuit and over current: Yes | Yes | complied | Complied | Compliant — AC overload, DC over-current and hardware-level OCP included. | Yes | Overcurrent/overload protection; thresholds not supplied
Protection Functions | 71 | Anti-islanding | Mandatory | Complied | Complied | Complied | Anti-islanding: Yes | Yes | complied | Complied | Compliant — Anti-islanding with UL-compliant trip points. | Yes – anti-islanding protection | IEC 62116 anti-islanding compliance
Protection Functions | 72 | Insulation | Continuous monitoring | Complied | Complied | Complied | Ground fault monitoring: Yes | Yes - Optional | complied | Complied | To be add and confirm in the V0.1 version— DC-side protection provided; continuous insulation monitoring | Yes – insulation detection | Online insulation detection
Protection Functions | 73 | Thermal / overload | Integrated | Complied | Complied | Complied | AC & DC over voltage and temperature: Yes | Yes | complied | Complied | Compliant — Over-temperature and AC overload / thermal protection integrated. | Yes – over-temperature and overload protection | Over-temperature and 110% overload protection
Control Functions | 74 | P/Q control | Four-quadrant | Complied | Complied | Complied | Four quadrant P/Q | Yes | complied | Complied | Compliant — Four-quadrant P/Q control (per PQ curve). | Yes – active/reactive power control | Four-quadrant P/Q control; PQ curve supplied
Control Functions | 75 | Frequency-Watt | Droop & FFR | Complied | Complied | Complied | Power reduction / FRT | Yes | complied | Complied | Compliant — Frequency-Watt droop and FFR supported (UL 1741 SA). | Primary frequency control available; frequency-Watt terminology not explicit | Frequency-Watt droop/FFR not stated
Control Functions | 76 | Ramp control | Up/down configurable | Complied | Complied | Complied | Configurable (active power limitation) | Yes | complied | Complied | Compliant — Configurable up/down ramp control. | Yes | Ramp rate settable in PCS
Control Functions | 77 | Mode transition | Seamless GFL ↔ GFM | Complied | No seamless transission | Can be discussed during detailed engg. | Not specified in datasheet | 160~200ms | complied | Complied | Compliant — GFL + GFM platform; seamless GFL<->GFM transition to be confirmed by test. | Grid-connected/island modes; charge/discharge conversion ≤20 ms | GFL↔GFM seamless transition not stated
Power Quality | 78 | Current THD | < 3 % at rated | Complied | Complied | Complied | < 3 % | Yes | <3% at rated power | Complied | Compliant — THDi < 3% at rated power (IEEE 1547, <5% TDD). | <3% at nominal/rated power | THDi <3% at rated power
Power Quality | 79 | Individual harmonic | IEEE 519 limits | Complied | Complied as per CEA | Complied | Not specified in datasheet | CEA 2022 latest regulation | complied | Complied | Compliant — IEEE 519 harmonic limits listed in certifications. | IEEE 519 certificate; individual harmonic values not stated | IEEE 519 numerical individual harmonic values not stated
Power Quality | 80 | Flicker | Within IEC limits | Complied | Complied | Complied | Not specified in datasheet | Yes | complied as per Latest CEA guidelines | Complied with EN 50549-2 and EN 50549-10 | Compliant | CEA/IEEE certification supplied; numerical flicker result not stated | Flicker compliance not stated
Power Quality | 81 | Voltage unbalance | Managed |  | No | Complied | Not specified in datasheet | Yes | complied as per Latest CEA guidelines | ±10% | Compliant | <2% voltage unbalance factor in off-grid operation | Voltage unbalance not stated
Reliability | 82 | MTBF | Documented | Will submitt | Will be shared up on receipt of order | Document will be shared during detailed engg. | Not specified in datasheet | Yes | kindly refer report for MTBF | Complied | Compliant | NA – MTBF not stated | MTBF not stated
Reliability | 83 | MTTR | Documented | Will submitt | Will be shared up on receipt of order | Document will be shared during detailed engg. | Not specified in datasheet | Yes | NA | Complied | Compliant | NA – MTTR not stated | MTTR not stated
Reliability | 84 | Component derating | Documented margins | Document Attached | Cannot be shared, confidential | Document will be shared during detailed engg. | Not specified in datasheet | DDE | can be shared later | Not available | Compliant | Ambient/altitude derating stated; component-specific derating not stated | Ambient/altitude derating stated; component-level margins not stated
Testing Regime | 85 | Type test | Documented | Attached | Complied | Document will be shared during detailed engg. | Not specified in datasheet | Yes | complied | Complied | In-Progress | Yes – multiple product certificates | Type-test certificates supplied/referenced; complete test dossier not supplied
Testing Regime | 86 | Routine test | Documented | Attached | Complied | Document will be shared during detailed engg. | Not specified in datasheet | Yes | complied | Complied | In-Progress | Not stated | Routine test not stated
Testing Regime | 87 | FAT | Pre-shipment | Will submitt | Complied | Complied | Not specified in datasheet | Yes | complied | Complied | In-Progress | Not stated | FAT not stated
Testing Regime | 88 | SAT | Post-install | Will submitt | SAT as per Hoymiles SAT procedure | Complied | Not specified in datasheet | Yes | complied | Complied | In-Progress | Not stated | SAT not stated
Testing Regime | 89 | Grid-code test | Compliance | CEA certification attached | Reports will be shared | Complied | Not specified in datasheet | Yes | complied | Complied | In-Progress | Yes – CEA certification testing | CEA/grid-code compliance stated; detailed grid-code test report not supplied
Warranty & Service | 90 | Standard warranty | ≥ 5 years | Standard 5 years ectended up to 20 years | Will be discussed during commercials | Standard warranty 5 years | Warranty extensions available | 5 Years | standard 5 years of warranty | Complied | Compliant | Not stated | Warranty not stated
Software / Firmware / OTA | 91 | Control APIs | Documented, versioned | For SCAD & EMS control we have the Modbus register map | Modbus mapping details of PCS will be shared | Will be shared during detailed engg. | Modbus/Profinet/Ethernet IP; remote monitoring | DDE | Kindly refer MODBUS communication document which will be shared later |  | In-Progress | PSSE/PSCAD control interfaces supplied; API/Modbus detail document not included in provided files | Modbus/communication interfaces documented; full control API/register map not supplied
Software / Firmware / OTA | 92 | OTA channel | authenticated | Yes | Not available | Will be shared during detailed engg. | Remote monitoring available | DDE | complied |  | In-Progress | Not stated | OTA channel not stated
0

## EFFICIENCY
-> curve_efficiency.csv
vendor | load_pct | eff_pct
Newen | 10 | 99.18
Newen | 25 | 99.28
Newen | 50 | 99.16
Newen | 75 | 98.99
Newen | 100 | 98.81
Inovance | 10 | 96.6
Inovance | 25 | 98.22
Inovance | 50 | 98.6
Inovance | 75 | 98.59
Inovance | 100 | 98.48
Inovance | 10 | 96.35
Inovance | 25 | 98.05
Inovance | 50 | 98.47
Inovance | 75 | 98.49
Inovance | 100 | 98.39
Inovance | 10 | 96.28
Inovance | 25 | 97.99
Inovance | 50 | 98.44
Inovance | 75 | 98.47
Inovance | 100 | 98.38
Kehua | 100 | 99

## PQ
-> curve_pq.csv
vendor | p_pct | q_lead_pct | q_lag_pct
Hoymiles | 2500 | 2500 | -2500
Sineng | 1300 | 1300 | -1300
Delta | 1250 | 1250 | -1250
Newen | 2749 | 2749 | -2749
Hopewind | 2500 | 2500 | -2500
Inovance | 2500 | 2470 | -2470
Fimer | 2500 | 2500 | -2500
Sifang | 2500 | 2500 | -2500
Kehua | 2500 | 2500 | -2500

## TEMP_DERATE
-> curve_temp_derate.csv
vendor | ambient_c | power_pct
Hopewind | 51 | 100
Hoymiles | 40 | 110
Hoymiles | 51 | 100
Delta | 30 | 110
Delta | 51 | 100
FIMER | 25 | 100
FIMER | 35 | 97.24
FIMER | 50 | 88.4
Newen | 25 | 110
Newen | 35 | 106
Newen | 51 | 100
Sineng | 40 | 110
Sineng | 51 | 100
Sineng | 55 | 82.24
Inovance | 45 | 110
Inovance | 55 | 100
Enerzolve | 45 | 100
Sifang | 35 | 110
Sifang | 50 | 100
Kehua | 30 | 110
Kehua | 45 | 100
Kehua | 55 | 50

## VOLTAGE_DERATE
-> curve_voltage_derate.csv
vendor | dc_min_v | power_pct
Hopewind | 1000 | 2500
Hopewind | 1000 | 2500
Hoymiles | 1000 | 2357.5
Hoymiles | 1060 | 2750
Hoymiles | 1500 | 2750
Delta | 1100 | 1250
FIMER | 978–1100 | 2500
Newen | 551 | 1394
Newen | 643 | 1653
Newen | 1038 | 2749
Newen | 1196–1500 | 3187
Sineng | 1000–1500 | 1300
Inovance | 1000–1500 | 2500
Enerzolve | 1000–1500 | 2500
Sifang | 1000–1500 | 2500
Kehua | 1060 | 2500
Kehua | 1500 | 2500

## LVRT_HVRT
-> curve_lvrt_hvrt.csv
vendor | type | time_ms | voltage_pu
Hopewind | LVRT | 0 | 1
Hopewind | LVRT | 150 | 0.85
Hopewind | LVRT | 1000 | 1
Hopewind | LVRT | 0 | 1
Hopewind | LVRT | 150 | 0.85
Hopewind | LVRT | 1000 | 1
Hopewind | LVRT | 0 | 1
Hopewind | LVRT | 150 | 0.5
Hopewind | LVRT | 1000 | 1
Hopewind | LVRT | 0 | 1
Hopewind | LVRT | 150 | 0.5
Hopewind | LVRT | 1000 | 1
Hopewind | HVRT | 0 | 1
Hopewind | HVRT | 150 | 1.1
Hopewind | HVRT | 1000 | 1
Hopewind | HVRT | 0 | 1
Hopewind | HVRT | 150 | 1.1
Hopewind | HVRT | 1000 | 1
Hopewind | HVRT | 0 | 1
Hopewind | HVRT | 150 | 1.2
Hopewind | HVRT | 1000 | 1
Hopewind | HVRT | 0 | 1
Hopewind | HVRT | 150 | 1.2
Hopewind | HVRT | 1000 | 1

## AUX_CONSUMPTION
-> curve_aux.csv. Fill aux_kw.
vendor | aux_kw
Hopewind | 5.5
Hoymiles | 3.02
Newen
FIMER
Delta
Sineng
Inovance | 7.8
ENERZOLVE
Sifang
Kehua | 4.3414

## CERTIFICATES
-> curve_certs.csv. Put 'Yes' where cert held.
vendor | IEC-62116 | IEC-62909 | IEC-62910 | IEC-60068 | IEC-61683 | IEC-60529 | IEC-61727 | IEC-61000 | IEC-62477 | IEC-61439 | IEC-60947 | IEEE-519 | IEEE-1547 | CEA-2022
Hopewind | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes
Hoymiles | Yes |  |  | Yes | Yes |  | Yes | Yes | Yes |  |  |  |  | Yes
Delta
FIMER | Yes |  | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  |  | Yes
Newen | Yes |  |  | Yes |  |  |  |  | Yes | Yes | Yes |  |  | Yes
Sineng | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  |  | Yes |  | Yes
Inovance | [7 empty] | Yes | Yes |  |  |  |  | Yes
ENERZOLVE
Sifang |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  |  | Yes |  | Yes
Kehua | Yes |  |  | Yes |  |  | Yes | Yes | Yes

## CHART_POINTS
-> chart_points.csv
chart | vendor | x | y
derate | Hopewind | 51 | 2500
derate | Hoymiles | 40 | 2750
derate | Hoymiles | 51 | 2500
derate | Delta | 30 | 1375
derate | Delta | 51 | 1250
derate | FIMER | 25 | 2500
derate | FIMER | 35 | 2431
derate | FIMER | 50 | 2210
derate | Newen | 25 | 3024
derate | Newen | 35 | 2912
derate | Newen | 51 | 2749
derate | Sineng | 40 | 1375
derate | Sineng | 51 | 1250
derate | Sineng | 55 | 1028
derate | Inovance | 45 | 2750
derate | Inovance | 55 | 2500
derate | ENERZOLVE | 45 | 2500
dcwin | Hopewind | 1000 | 1500
dcwin | Hoymiles | 1000 | 1500
dcwin | Delta | 1100 | 1500
dcwin | FIMER | 978 | 1500
dcwin | Newen | 551 | 1500
dcwin | Sineng | 1000 | 1500
dcwin | Inovance | 1000 | 1500
dcwin | ENERZOLVE | 1000 | 1500
overload | Hopewind | cont | 110
overload | Hopewind | 10 | 120
overload | Hopewind | 1 | 150
overload | Hoymiles | cont | 110
overload | Delta | cont | 110
overload | Newen | 10 | 110
overload | Sineng | 600 | 110
overload | Sineng | 120 | 120
eff_peak | Hopewind |  | 98.5
eff_euro | Hopewind
eff_peak | Hoymiles |  | 99
eff_euro | Hoymiles |  | 98.5
eff_peak | Delta |  | 99
eff_euro | Delta |  | 98.5
eff_peak | FIMER |  | 98.8
eff_euro | FIMER |  | 98.6
eff_peak | Newen |  | 99.21
eff_euro | Newen |  | 99.03
eff_peak | Sineng |  | 99
eff_euro | Sineng |  | 98
eff_peak | Inovance |  | 99
eff_euro | Inovance |  | 98.3
eff_peak | ENERZOLVE |  | 98.5
eff_euro | ENERZOLVE |  | 98.3
eff_peak | Kehua |  | 99
eff_euro | Kehua |  | 98.5

## IGBT_INFO
IGBT make, module type & failure rate (FIT). Fill cream cells. -> igbt_info.csv
vendor | igbt_make | failure_rate_fit | module_type
Hopewind | Fuji | NA | 2MBI800XNE120-50, 1200 V / 800 A IGBT, I-type 3-level
Hoymiles | Infineon / Fuji / CRRC / Starpower | NA | FF450R12ME4 (Infineon), 2MBI600XNG120-50 (Fuji), TG450HF12M1-G3A00 (CRRC), GD450HFX120C6SB (Starpower), and TG450HF12M1-S3A00 (CRRC) as alternative IGBT options. Exact production selection should be confirmed with Hoymiles.
Delta | Infineon | NA | FF1000R12KE7, 1200 V / 1000 A IGBT power module
FIMER | Infineon / Fuji | NA | NA
Newen | NA | NA | NA
Sineng | NA | NA | NA
Inovance | NA | NA | NA
ENERZOLVE | NA | NA | NA
Sifang | NA | NA | NA
Kehua | Infineon / Fuji | NA | FF900R series, 1200 V/900 A; 2MBI800 series, 1200 V/800 A

## IGBT_TEMP
IGBT junction temp vs % capability. Fill performance_pct. -> curve_igbt_temp.csv
vendor | junction_temp_c | performance_pct | data_type | notes
Hopewind | 112.1 | 100 | Actual operating point | Full-power operation at 51°C ambient; documented Tj = 112.1°C
Hoymiles | 150 | NA
Delta | 25 | NA
FIMER | 25 | NA
Newen | 25 | NA
Sineng | 25 | NA
Inovance | 25 | NA
ENERZOLVE | 25 | NA
Sifang | 25 | NA
Kehua | 25 | NA

## HOW TO USE
PCS Master (V6_1 + aux + certs)
Edit | cream cells on any tab
Generate | python xlsx_to_csv_all.py PCS_Master_All.xlsx
Upload | all CSVs + index.html to GitHub, hard-refresh
AUTOMATION
chart_points.csv is now AUTO-GENERATED from the MATRIX when you run the converter.
You never edit chart_points manually. Add a vendor to MATRIX -> charts include it automatically.